## Hydro
CAPACITY ANALYSIS WORKSHEET FOR HYDROPNUMATIC SYSTEMS
User inputs data into orange cells. Results are calculated in tan cells. All pressures calculated in absolute units, i.e., equations contain 14.7 psi added to gauge pressures.
Effective Volume | [5 empty] | Horizontal Tank Volumes
| 1pre-charge pressure, P1 |  | psi, gage |  |  | Inside Diameter |  | inches
| 2cut-in pressure, P2 |  | psi, gage |  |  | Inside Side Wall Length |  | inches
| cut-out pressure, P3 |  | psi, gage |  |  | End Caps |  | select
| Gross volume of hydro tank(s), Vt |  | gallons |  |  | Water level |  | inches above bottom
| Effective draw-down volume, Ve | 0 | gallons |  |  | Water Volume | #DIV/0! | gallons
| acceptance factor | #DIV/0!
1Pre-charge pressure cannot be greater than cut-in pressure for pump to start, and optimal setting is about 2-4 psi below cut-in pressure to maintain system pressure.
2Calculate Total Dynamic Head in distribution system to determine acceptable cut-in pressure. Note: Volume below amount needed to maintain minimum system pressure unavailable as storage.
Cycle Time
|  | gpm | times in minutes |  |  | Cycles/hr Nc
| Pump into tank, I |  | Pump ON | Pump OFF | Cycle Time
| Demand, O |  | Pump Off | no demand | no demand | no demand
| net flow, gpm | pump=demand | * Maximum pump cycle = |  |  | #DIV/0!
|  |  | Pump Off | = Ɨ Minimum pump run
* Maximum pump cycle occurs @ demand = half pump capacity. |  | Ɨ Minimum pump run times: 1 min. < 5 hp ≥2 min., or manufacturer's recommendation.
Pump Selection
|  | Total head: | Low Pressure |  | High Pressure
|  |  | psi | feet | psi | feet
| Tank inlet above measuring point, ft |  | 0 | 0 | 0 | 0
| Measuring point to static water level, ft |  | Use positive values. Approximate operating point for the pump. Find points between low and high head on pump curve and use median for pump capacity.
Drawdown below static water level, ft
Dynamic head, pump to tank, ft
Additional information and requirements for hydro system sizing may be found at:
DEP Rules
DEP Capacity Analysis Guidelines
Recommended Standards for Waterworks
Pumped water systems article - National Driller
Drawdown calculations - National Driller
Multiple tank systems - National Driller
Water Systems Council
Technical Manual - Peerless Pump Company
Technical Manual-Goulds Pumps
Ve/((I-O)) + Ve/O = pump on + pump off
A hydropneumatic tank is a pressure vessel connected to a water system and containing water in the lower portion and air in the top portion. When the tank is being filled from the pump, the water volume increases and the air is compressed. When the pump is turned off, the compressed air maintains pressure in the system until the water drains and the pressure drops. Hydropneumatic tanks typically only provide very limited equalization and therefore should not be considered to be effective storage facilities for such purposes. Whenever possible, hydropneumatic tanks should not be a substitute for a properly sized atmospheric storage tank. 1. Rule 62-555.320(20) in the Florida Administrative Code (F.A.C.) New hydropneumatic tanks, including bladder - or diaphragm-type tanks, shall be designed and constructed in accordance with Section 7.2 in Recommended Standards for Water Works as incorporated into Rule 62-555.330, F.A.C., except that: (a) The tanks need not be housed. (b) Tanks ...shall have an automatic air or pressure relief valve. (c) Bladder- or diaphragm-type tanks need not have an access manhole, water sight glass, or means for adding air other than a recharging valve. Refer to: 62-555.350(2) for maintenance requirements, 62-555.350(12)(c) for inspections, 62-555.520(4)(a)3c for water demand. See Storage Requirements tab to determine if additional storage is needed. 2. Recommended Standards for Water Works (adopted as rule in F.A.C. 62-555.330(3)) 7.2 HYDROPNEUMATIC TANK SYSTEMS Hydropneumatic (pressure) tanks, when provided as the only water storage are acceptable only in very small water systems. Systems serving more than 150 living units should have ground or elevated storage designed in accordance with Section 7.1 or 7.3. Hydropneumatic tank storage is not to be permitted for fire protection purposes. Pressure tanks shall meet ASME code requirements or an equivalent requirement of state and local laws and regulations for the construction and installation of unfired pressure vessels. Non-ASME, factory-built hydropneumatic tanks may be allowed if approved by the reviewing authority. Note: All new PWS hydropneumatic tanks must meet either the ASME code requirements for unfired pressure vessels or ANSI/Water Systems Council (WSC) Standard PST 2000, Pressurized Water Storage Tank. ANSI/WSC PST 2000 applies only to tanks with volumes not exceeding 120 gallons, with a maximum factory pre-charge pressure of 40 psig, and with a maximum working pressure of 75 – 140 psig. The WSC maintains a list of tanks meeting WSC PST 2000 . See link below. 7.2.1 Location The tank shall be located above normal ground surface. 7.2.2 System sizing a. The capacity of the wells and pumps in a hydropneumatic system should be at least ten times the average daily consumption rate (Peak Instantaneous Demand) . Note: depending on the deisgn criteria, PID may also be determined using USACE "Design of Small Water Systems", Figure 4-1. In some instances conventional hydro tanks without added air may not allow minimum pump cyyle time. b. The gross volume of the hydropneumatic tank, in gallons, should be at least ten times the capacity of the largest pump, rated in gallons per minute. For example, a 250 gpm pump should have a 2,500 gallon pressure tank, unless other measures (e.g., variable speed drives in conjunction with the pump motors) are provided to meet the maximum demand. c. Sizing of hydropneumatic storage tanks must consider the need for disinfectant contact time. 7.2.3 Piping The hydropneumatic tank(s) shall have bypass piping to permit operation of the system while the tank is being repaired or painted. 7.2.4 Appurtenances Each tank shall have an access manhole, a drain, and control equipment consisting of a pressure gauge, water sight glass, automatic or manual air blow-off, means for adding air, and pressure operated start-stop controls for the pumps. A pressure relief valve shall be installed and be capable of handling the full pumpage rate of flow at the pressure vessel design limit. Where practical the access manhole should be 24 inches in diameter. * The effective, or drawdown volume is the amount of useable water that can be drawn from a hydro-pneumatic tank from the time the pressure switch cuts out, turning the pump off, until the pressure switch cuts back in, turning on the pump, i.e., the , the amount of water delivered between pump shutdown and start. The amount of drawdown capacity is determined by Boyle’s Law, which states that as the volume of the air cushion in a tank decreases, the pressure of that air cushion increases. Boyle's Law expresses general air and water volumes in a hydropneumatic tank. Where : Ve= effective volume Vt = gross tank volume P1 = pre-charge pressure P2 = cut-in pressure P3 = cut-out pressure * A small water volume may exist below cut-on pressure and pressure needed to maintain minimum system pressure, depending on pre-charge. Notes: Pump starts should be no more than 7-10 starts per hour, and run time at least 1-2 minute minutes, depending on horse power and pump manufacturer's recommendations. Verify minimum flow rate around motor for proper cooling. Well with high static level may require throttling valve to prevent upthrust. Refer to manufacturer's recommendations. Pump must be placed at least 5-feet below drawdown level, and at least 10-feet above bottom of well.
"Ve=" VtP1((P3-P2)/P3P2)

## Storage
CAPACITY ANALYSIS WORKSHEET FOR HYDROPNUMATIC SYSTEMS
| User inputs data into orange cells. Calculation results in tan cells. | [5 empty] | conversions:
|  |  | input gpd | Peak Factor | Peak Factor Range |  | gpm*1440=gpd |  | gpd/1440=gpm
[5 empty] | Range |  |  | gpm |  | gpd
|  | Average Day Demand (ADD) |  |  |  |  | 0 | gpd | 0 | gpm
|  | Maximum Day Demand (MDD) | 0 | 2 | 1.5-3.5 (or DMDD) |  |  | gpm, needed fire flow rate
|  | Peak Hourly Demand (PHD) | 0 | 4 | 2.0-7.0 |  |  | minutes, needed fire flow duration
|  | Peak Instantaneous Demand (PID) | 0 | 10 | 110 |  | 0 | gallons, fire storage
|  | Pump flow to tank | 0
|  | 2Storage needed for peak-hour demand | none | gallons
|  | 2Storage for peak-instantaneous demand | none | gallons | pump=demand | gpm, net flow from Hydro page
1Depending on deisgn criteria, PID may also be determined using USACE "Design of Small Water Systems", Figure 4-1.
2Refer to F.A.C. 62-555.320(19)(b)2 above for applicable storage requirements.
Persons preparing a capacity analysis report should consider, and coordinate appropriate aspects of the report with, applicable local government comprehensive plans and applicable regional water supply plans prepared by water management districts. Rule 62-555.320(6): The total capacity of all water source and treatment facilities connected to a water system shall at least equal the water system's design maximum-day water demand (including design fire flow demand if fire protection is bring provided). Additionaly, 62-555.320(19) storage requirements apply. For small hydro systems: Rule 62-555.320(19)(b)2… For water systems that are using hydropneumatic tanks and that were permitted before August 28, 2003, no finished-water storage capacity is required if the source, treatment, and finished-water pumping facilities themselves can meet peak-hour water demand for at least four consecutive hours. For systems that are using hydropneumatic tanks, the well pump and treatment facilities almost always are designed to meet at least the peak-hour demand (which generally is approximately four times the annual average daily demand). If the well pump and treatment facilities cannot meet the peak-hour demand, the required effective storage volume in the hydropneumatic tank is: {(peak-hour demand, gpm) – (well pump capacity, gpm)} * (240 minutes) For water systems that are using hydropneumatic tanks and that are permitted after August 28, 2003, no finished-water storage capacity is required if the source, treatment, and finished-water pumping facilities themselves can meet peak-hour water demand for at least four consecutive hours and can meet peak instantaneous demand for at least 20 minutes. For systems that are using hydropneumatic tanks, the well pump and treatment facilities almost always are designed to meet a least the peak-hour demand (which generally is approximately four times the annual average daily demand) and should be designed to meet the peak instantaneous demand (which generally is approximately 10 times the annual average daily demand and hence the recommendation in Section 7.2.2a of Recommended Standards for Water Works). If the well pump and treatment facilities can meet the peak-hour demand but cannot meet the peak instantaneous demand, the required effective storage volume in the hydropneumatic tank is: {(peak instantaneous demand, gpm) – (well pump capacity, gpm )} * (20 minutes) Projections of maximum-day or peak-hour water demand usually are made by multiplying projections of annual average daily water demand by an appropriate peaking factor. Peaking factors vary depending upon PWS size, the extent of commercialization and industrialization, etc. Therefore, maximum-day to average-day peaking factors should be determined specifically for each PWS by looking at past water production data for the PWS. (According to Water Distribution Systems Handbook, which is incorporated as an engineering reference into Rule 62-555.330, F.A.C., maximum-day water demand typically ranges from 1.5 to 3.5 times average daily water demand.) Peak-hour to average-day peaking factors should be determined specifically for each PWS based upon flow measurement data if possible; but oftentimes, peak-hour to average-day peaking factors will have to be estimated. (According to Water Distribution Systems Handbook, peak-hour water demand typically ranges from 2.0 to 7.0 times average daily water demand.) Finished-water storage need is the finished-water storage capacity needed for operational equalization to meet peak water demand and comply with subsection 62-555.320(19), F.A.C., plus finished-water storage capacity needed to meet any fire-flow requirements. Finished-water storage needed to meet fire-flow requirements can be calculated using the equation… FS = (NFFR + MDD – TPC) (NFFD) where FS = fire storage, NFFR = needed fire-flow rate, MDD = maximum-day demand, TPC = treatment plant capacity (i.e., total maximum-day or peak capacity of a PWS’s treatment plants), and NFFD = needed fire-flow duration. Refer to the DEP "Capacity Analysis Report Guideline (2004) for additional information.

## Dose
CHLORINE FEED RATE
Chlorine demand. If no data, assume a value in the 5-10 ppm range.
Feed pump output:
Feed rate = well pump output rate (gpm) * dosage (ppm) * 1440 (min/day) / [solution strength, % * (10,000 ppm/1% str.)]
Where:
Feed Rate = feed pump output rate (gpd)
Well Output = average well pump output (gpm) (assumed constant)
D = required dosage (demand + desired residual in distribution system, ppm)
% Cl sol'n = percentage of NaOCl in solution (off-the-shelf bleach is typically about 5%)
SS = solution strength (1 %/10,000 ppm)
User inputs data into orange cells.
Feed Rate Calcluations:
| *Well Output | 0 | gpm
| D |  | ppm
| % Cl sol'n |  | percent NaOCl
| SS | 0 | ppm
| Feed Rate | 0 | gpd
* from Hydro Page
Chlorine Reservior Calculations:
|  | Reservoir capacity: |  | gallons (input tank size)
|  | Demand, | pump on, | pump amt | refill time,
|  | gallons | min | gallons | days
| *Max. Day | 0 | #DIV/0! | #DIV/0! | need dose
| *Avg. Day | 0 | #DIV/0! | #DIV/0! | need dose
*From Storage page